Specifications and Regulations for Aboveground Storage Tanks (ASTs)

- ASTs are regulated by Manitoba Environment if:

  - they are greater than or equal to 1000 gallons; or

  - a problem is noticed and reported to Manitoba Environment.

- ASTs found in Winnipeg are regulated by Winnipeg Fire Department under the National Fice Code (NFC).  If the folf course is not located in a city (e.g. Wpg, PLAP, or Brandon), ASTs are regulated by the Department of Labour under the NFC and/or by Manitoba Environment if the above mentioned criteria exist.

- Gravity-fed ASTs are allowed ona  course legally provided all of the following conditions are met:

a)  	the ASTs are ULC approved (with tags on tank);

b) 	the AST stand has an approved two hour fire rating;

- and secondary containment is present (i.e. dike).

- Dikes are required for all ASTs.  The only exception to this law is if the AST is double walled (i.e. self-containing or double-walled ASTs do not require a dike).

- Dikes must be made of:

  - concrete

  - steel

  - special liner with crushed gravel on top

- Dikes must:

  - be able to contain not less than 110% of the volume of the largest AST within it

  - be graded to collection sump in one corner

  - be free of all vegetation within dike area and around the perimter of the dike

- Nothing can be stored in the dike area (e.g. boards, gerry cans, empty containers, etc.).

- If the AST is double walled it must meet all of the following conditions:

a)	tank must be ULC approved (with tags on tank);

- bollards must be present aroud tank;

- and a concrete pad with a 1 – 2% grade or compacted gravel must be beneath the tank.

- Non-gravity fed ASTs must have bollards around them and be placed on a concrete pad.

- All ASTs must be at least 3 meters from the property line.